REPORT ON INVESTIGATION AND RESOLUTION OF NON-FUNCTIONING CCTV SYSTEMS

In Reference to:

Order No.: 74 of 2025

Dated: 02-09-2025

Subject: Investigation and Resolution of Non-Functioning CCTV Systems in the Institution.

- Introduction

As directed under Order No. 74 of 2025, the CCTV network across the institution was inspected, analysed, and rectified to restore full operational functionality. The Institutional CCTV Committee undertook a detailed investigation into the issues causing non-functioning and fluctuating CCTV feeds from multiple locations within the campus.

- Initial Observations

The CCTV systems installed by the previous vendor NextGen were found to be continuously fluctuating and unstable. Despite repeated attempts, the vendor was unable to rectify the outage or ensure stable functioning of the network. Therefore, TechBuddy was contacted for professional analysis and troubleshooting.

- Technical Analysis by TechBuddy

a) Network Instability:

Multiple network loops, unnecessary junction points, and faulty infrastructure links were causing severe data fluctuations. Improper OFC terminations and non-uniform switch configurations contributed to packet loss and instability.

b) Hardware Limitations:

Several existing hardware devices were outdated, malfunctioning, or incompatible with the current load.

c) Improper Network Segmentation:

All cameras across blocks were using common network paths without proper segregation, leading to congestion.

- Corrective Measures Taken

a) Network Restructuring:

The CCTV network was reorganized into four major blocks:

- Academic Block

- New Block

- Administration Block

- Canteen / Wood Technology Area

b) Fibre Network Optimization:

- Data feeds from cameras in New Academic Block, Academic Block, Canteen, and Wood    Technology Area were consolidated.

- These feeds were connected via a single OFC line to the Auditorium in the academic block.

- From the Auditorium, data was transferred via 6-core OFC to a 16-port Gigabit Switch.

- Five media converters were installed for fibre-to-LAN conversion

c) Removal of Junctions & Loops:

All unnecessary network loops and junctions were removed, stabilizing the entire system.

d) Network Testing:

The whole network was tested thoroughly and all cameras are now functioning successfully.

- Additional Work in Computer Department

Due to lab renovation, the CCTV control system and NVR were shifted from Programming Lab-1 to the Staff Room. The following items are required:

• Wall mount bracket

• HDMI cable

• Wireless mouse

• Additional Cable

- Additional work  in boys hostel:

As per the directions issued by the Principal, five additional IP cameras, one PoE switch, and the required cabling are to be installed in the Boys’ Hostel, KGP Srinagar, to ensure proper surveillance of the hostel premises.

Hence, for carrying out the above-mentioned work, the committee hereby recommends the requirement of the following items

| S.No | Items required | Quantity |
| --- | --- | --- |
|  | Fiber optic junction box | 4 |
|  | OFC Patch Cable | 11 |
|  | RJ45 connectors | 20 |
|  | Fiber protection Sleeve | 1 |
|  | Fiber 12 V adpater | 1 |
|  | Power distribution Unit | 1 |
|  | RacK Tray | 3 |
|  | 16-port Giga switch | 1 |
|  | OFC cable | 198 mts |
|  | Power adapter 5V, 2 amp | 1 |
|  | Media Converter | 1 |
|  | USB extension Cable 1.5 m | 1 |
|  | Wireless Mouse | 1 |
|  | Fiber HDMI 3 mts | 1 |
|  | Wall bracket | 1 |
|  | IP Cameras | 5 |
|  | PoE Switch | 1 |
|  | Double jacket outdoor cable | 150 mts |

Signatures of Committee Members:-

- Mr. Umer Mushtaq  ( Electrician)                                             ________________________________

- Mr. Waseem       (Electrician)                                                     ________________________________

- Er. Farooq Ahmad Bhat ( Demonstrator)                              ________________________________

- Er. Irfan Ahmad Sofi  ( Demonstrator)                                   _________________________________

- Er. Inhas Ashraf   (Lecturer-I)                                                  _________________________________

- Er. Shabir Ahmad Ahnager  (Lecturer-I)                              _________________________________